## Slide 1: EEL 5245 POWER ELECTRONICS I Lecture #11 Ch 3:Non-Sinusoidal Systems and Harmonics Overview

## Slide 2: Discussion Topics
Real World Power System Data
  What is its harmonic content? And why?
Decomposition of non-sinusoidal waveforms into Fourier Series
Significant Effects of Harmonics on Power System
Power Parameters for Non-sinusoidal Systems
Harmonics in Three Phase Systems
Regulatory Standards for Harmonic Content
PC Power Supply Analysis

## Slide 3: Nature of Modern Electrical Loads
Historically, electrical loads in the power system were predominately linear (purely sinusoidal input voltage draws a sinusoidal current in a linear load)
  Incandescent lighting, motor loads (cooling)
Semiconductor advances paved the way for boom in electronic equipment development
  PC, laptops, iPhones, Audio/Video Equipment, Lighting Controls, etc.
These electronic loads are generally nonlinear (purely sinusoidal line voltage draws distorted, non-sinusoidal, line current)
The nonlinear load means the current waveform, while periodic, is not sinusoidal and has harmonics
Harmonic content is a result of proliferation of nonlinear loads in the modern power system.

## Slide 4: Nature of Modern Electrical Loads Real Data Examples
Note-
Voltage nearly sinusoidal,
Current moderately distorted

## Slide 5: Harmonic Content of Full-Wave Rectifier with Filtering Cap
Most electronic loads employ a “peak detection rectifier” at their front end
Source current present only when input sinusoidal exceeds DC voltage across capacitor

## Slide 6: Linear Loads – RL Circuits
(b) Phasor Diagram
(a) Simple Liner RL

## Slide 7: None-Linear Loads – Power Electronics Circuits
(b) Distortion current
(a) Source voltage and current

## Slide 8: None-Linear Loads – Power Electronics Circuits
Example of Distortion current

## Slide 9: Fourier Analysis for Harmonics Calculation
Periodic waveforms can be resolved into an infinite Fourier Series
Series is comprised of a summation of pure sinusoids each with frequencies that are integer multiples of the fundamental frequency of the periodic waveform
Where constant Fo and the coefficients an and bn given by,

## Slide 10: Decomposition of v & i into Harmonic Components
DC Component
Fundamental Component
Harmonic Components

## Slide 11: Most Significant Effects of Harmonics in the Power System
Harmonics reduced True Power Factor (add to RMS but do no real work)
  Less of power system capacity available with no benefit
EMI Created interferes with other equipment operation such as communications signals and control electronics in other devices
  Comm equipment doesn’t work well near harmonic generators
Neutral Current in 3 Phase Wye connected systems can be larger than phase current causing overloaded conductors
  Historically neutral conductors had been design with smaller ampacity than phase conductors
Only high end metering devices detect harmonic content
  If it doesn’t say “True RMS” it will read incorrectly for most electronic loads
Transformers and motors are subjected to additional heating due to harmonics
  K-Factor rated equipment for additional I^2*R Losses
Notes: K-Factor rated equipment:
What is K-Factor?
K-factor is a weighting of the harmonic load currents according to their effects on transformer heating, as derived from ANSI/IEEE C57.110. A K-factor of 1.0 indicates a linear load (no harmonics). The higher the K-factor, the greater the harmonic heating effects.
http://www.xitrontech.com/assets/002/5787.pdf

## Slide 12: Harmonics in the Power System

## Slide 13: Real Power and Harmonics

## Slide 14: Real Power and Harmonics

## Slide 15
Power Transfer – Different Harmonics

## Slide 16
Power Transfer – Same Harmonics

## Slide 17: Example – Average power calculation

## Slide 18: Example – Average power calculation(con’d)

## Slide 19: RMS Value of Nonlinear Waveform

## Slide 20: Power Factor Definition

## Slide 21: True Power Factor Definition

## Slide 22: Distortion Factor and THD

## Slide 23: DF vs. THD

## Slide 24: Harmonics in Three Phase Systems

## Slide 25: Harmonics in Three Phase Systems

## Slide 26: Harmonics in Three Phase Systems

## Slide 27: Harmonics in Three Phase Systems

## Slide 28: Neutral Currents in 3 Phase, Wye Connected Systems
Assuming a balanced load with no phase shift (V and I in phase)
Assuming line current composed of fundamental, 60Hz, and third harmonic, 180 Hz only (In practice other harmonics would be present
Third harmonic set at 33% of fundamental current amplitude
Assume power system fully loaded such that phase conductors are rated for 100 ARMS

## Slide 29: Neutral Currents in 3 Phase, Wye Connected Systems

## Slide 30: Harmonics in Three Phase Systems

## Slide 31: Standards Regulating Harmonic Content
US MIL-STD-461B
  US Military Standard (Mandatory)
  Harmonic limits now enforced by all US Armed Forces
International Electro-technical Commission Standard 555
  European Standard (Mandatory)
  Limits based on actual current values specified by harmonic number by class of equipment
IEEE 519
  US Suggested Guidelines by IEEE
  Harmonic limits are based on the ratio of fundamental component of load current to short circuit current at the utility interface point

## Slide 32: IEC 555: Class A limits

## Slide 33: IEEE-519 Current Limits, Low Voltage Systems

## Slide 34: IEEE-519 voltage limits

## Slide 35: PC Power Supply Analysis
To investigate the nature of Harmonics in the modern power system, the personal computer load is representative
  Quantity in service increasing in residential, commercial, and industrial use
    Not uncommon to have an office area with many PCs
  PC Power supply is Switch Mode Power Supply (SMPS) with peak detection rectifier at front end for rectification
    Moderate harmonic generator
For this analysis, experimental data is collected on a Pentium 4 Dell Machine, 80Gb Hard Drive, 250W Power Supply, and 19” CRT Monitor
Data is collected with a Fluke 41, Power Harmonics Analyzer

## Slide 36: PC Power Supply Analysis

## Slide 37: PC Power Supply Analysis

## Slide 38: PC Power Supply Analysis

## Slide 39: Fourier Analysis for Harmonics Calculation (
Periodic waveforms can be resolved into an infinite Fourier Series
Series is comprised of a summation of pure sinusoids each with frequencies that are integer multiples of the fundamental frequency of the periodic waveform

## Slide 40: Fourier Analysis for Harmonics Calculation
Trigonometric Form often used
  industrial test equipment uses this format
  FFT function gives complex form, angle derived assumes a cosine function is used to recreate f(t) so Sine and Cosine not interchangeable without proper shifting
    Note if function either even or odd, An reduces to either an (even) or bn (odd) and Thetan is either 0 (even) or -90 (odd)
Book
Correction
Pay attention to Quadrant

## Slide 41: Use of Symmetry in Fourier Analysis

## Slide 42: Observations on Symmetry
Can save alot of time
Converter circuit waveforms often not symmetric
Converter input current and voltage generally has symmetry
  Odd and Half Wave very common
  Be able to recognize this combination and its effect on Fourier Components on sight
In Industrial Power System (on AC side of things, most everything is odd with half wave symmetry, so no even harmonics and no DC value